*Table XY*

**Minimum time periods for which a V1G electric vehicle and an associated V1G electric vehicle supply equipment shall be capable of operating on different frequencies, deviating from a nominal value, without disconnecting from the network**

|  |  |
| --- | --- |
| **Frequency range** | **Time period for operation** |
| 47,5 Hz-48,5 Hz | 30 minutes |
| 48,5 Hz-49,0 Hz | 30 minutes |
| 49,0 Hz-51,0 Hz | Unlimited |
| 51,0 Hz-51,5 Hz | 30 minutes |
| 51,5 Hz-52,5 Hz | 10 seconds |